{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["废水比对","废水排放"],"not_rendered":{"external_links":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废水比对","index":0,"n_rows":11,"n_cols":14,"rows_kept":11,"merged":[[1,0,10,0],[1,1,5,1],[6,1,10,1]],"flags":["formulas_cached_only"]}
["任务名称","企业名称","名录类别","行业类别","执行标准名称","执行标准条目名称","监测点","监测项目","监测日期","样品类型","手动监测值","自动监测值","比对结果","技术要求"]
["江苏省妇幼卫生保健中心、南京儿童医院","江苏省妇幼卫生保健中心","水环境","医院","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水处理站排口","pH值","2024-08-28","实际样","7.4","7.5","0.1pH","绝对误差不超过±0.5pH"]
["江苏省妇幼卫生保健中心、南京儿童医院","江苏省妇幼卫生保健中心","水环境","医院","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水处理站排口","化学需氧量","2024-08-28","实际样","144","139","-3.47%","相对误差不超过±15%"]
["江苏省妇幼卫生保健中心、南京儿童医院","江苏省妇幼卫生保健中心","水环境","医院","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水处理站排口","化学需氧量","2024-08-28","实际样","151","143","-5.3%","相对误差不超过±15%"]
["江苏省妇幼卫生保健中心、南京儿童医院","江苏省妇幼卫生保健中心","水环境","医院","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水处理站排口","化学需氧量","2024-08-28","实际样","144","136","-5.56%","相对误差不超过±15%"]
["江苏省妇幼卫生保健中心、南京儿童医院","江苏省妇幼卫生保健中心","水环境","医院","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水处理站排口","化学需氧量","2024-08-28","标准样","268","250","-6.72%","相对误差不超过±10%"]
["江苏省妇幼卫生保健中心、南京儿童医院","南京市儿童医院","水环境","专科医院","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","化学需氧量","2024-08-28","实际样","144","136","-5.56%","相对误差不超过±15%"]
["江苏省妇幼卫生保健中心、南京儿童医院","南京市儿童医院","水环境","专科医院","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","化学需氧量","2024-08-28","实际样","137","128","-6.57%","相对误差不超过±15%"]
["江苏省妇幼卫生保健中心、南京儿童医院","南京市儿童医院","水环境","专科医院","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","化学需氧量","2024-08-28","实际样","142","131","-7.75%","相对误差不超过±15%"]
["江苏省妇幼卫生保健中心、南京儿童医院","南京市儿童医院","水环境","专科医院","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","化学需氧量","2024-08-28","标准样","250","255","2%","相对误差不超过±10%"]
["江苏省妇幼卫生保健中心、南京儿童医院","南京市儿童医院","水环境","专科医院","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","pH值","2024-08-28","实际样","6.9","7.0","0.1pH","绝对误差不超过±0.5pH"]

{"sheet":"废水排放","index":1,"n_rows":11,"n_cols":22,"rows_kept":11,"merged":[[1,0,10,0],[1,1,5,1],[6,1,10,1]],"flags":["formulas_cached_only"]}
["任务名称","企业名称","名录类别","行业类别","受纳水体","执行标准名称","执行标准条目名称","监测点","监测项目","监测日期","流量(m³/s)","水温(°C)","生产负荷(%)","进口浓度","排放浓度","上限","下限","单位","是否超标","超标倍数","备注","是否有评价限值"]
["江苏省妇幼卫生保健中心、南京儿童医院","江苏省妇幼卫生保健中心","水环境","医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水处理站排口","悬浮物","2024-08-28","","27.7","","","51","60","","mg/L","否","","","是"]
["江苏省妇幼卫生保健中心、南京儿童医院","江苏省妇幼卫生保健中心","水环境","医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水处理站排口","动植物油","2024-08-28","","27.7","","","0.91","20","","mg/L","否","","","是"]
["江苏省妇幼卫生保健中心、南京儿童医院","江苏省妇幼卫生保健中心","水环境","医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水处理站排口","pH值","2024-08-28","","27.7","","","7.4","9","6","无量纲","否","","","是"]
["江苏省妇幼卫生保健中心、南京儿童医院","江苏省妇幼卫生保健中心","水环境","医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水处理站排口","化学需氧量","2024-08-28","","27.7","","","146","250","","mg/L","否","","","是"]
["江苏省妇幼卫生保健中心、南京儿童医院","江苏省妇幼卫生保健中心","水环境","医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水处理站排口","石油类","2024-08-28","","27.7","","","0.18","20","","mg/L","否","","","是"]
["江苏省妇幼卫生保健中心、南京儿童医院","南京市儿童医院","水环境","专科医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","动植物油","2024-08-28","","28.2","","","0.11","20","","mg/L","否","","","是"]
["江苏省妇幼卫生保健中心、南京儿童医院","南京市儿童医院","水环境","专科医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","化学需氧量","2024-08-28","","28.2","","","141","250","","mg/L","否","","","是"]
["江苏省妇幼卫生保健中心、南京儿童医院","南京市儿童医院","水环境","专科医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","pH值","2024-08-28","","28.2","","","6.9","9","6","无量纲","否","","","是"]
["江苏省妇幼卫生保健中心、南京儿童医院","南京市儿童医院","水环境","专科医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","悬浮物","2024-08-28","","28.2","","","57","60","","mg/L","否","","","是"]
["江苏省妇幼卫生保健中心、南京儿童医院","南京市儿童医院","水环境","专科医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","石油类","2024-08-28","","28.2","","","0.27","20","","mg/L","否","","","是"]