{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["废水比对","废水排放"],"not_rendered":{"external_links":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废水比对","index":0,"n_rows":10,"n_cols":14,"rows_kept":10,"merged":[[1,0,9,0],[1,1,9,1]],"flags":["formulas_cached_only"]}
["任务名称","企业名称","名录类别","行业类别","执行标准名称","执行标准条目名称","监测点","监测项目","监测日期","样品类型","手动监测值","自动监测值","比对结果","技术要求"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","氨氮（NH3-N）","2024-10-31","实际样","1.44","1.42","-0.02mg/L","绝对误差不超过±0.3mg/L"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","氨氮（NH3-N）","2024-11-01","实际样","1.44","1.44","0mg/L","绝对误差不超过±0.3mg/L"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","氨氮（NH3-N）","2024-11-01","实际样","1.44","1.47","0.03mg/L","绝对误差不超过±0.3mg/L"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","氨氮（NH3-N）","2024-10-31","标准样","5.58","5.47","-1.97%","相对误差不超过±10%"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","pH值","2024-10-31","实际样","6.9","6.8","-0.1pH","绝对误差不超过±0.5pH"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","化学需氧量","2024-10-31","实际样","23.1","22.0","-1.1mg/L","绝对误差不超过±5mg/L"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","化学需氧量","2024-11-01","实际样","23.1","22.9","-0.2mg/L","绝对误差不超过±5mg/L"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","化学需氧量","2024-11-01","实际样","23.1","20.8","-2.3mg/L","绝对误差不超过±5mg/L"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","化学需氧量","2024-10-31","标准样","51.5","48.9","-5.05%","相对误差不超过±10%"]

{"sheet":"废水排放","index":1,"n_rows":7,"n_cols":22,"rows_kept":7,"merged":[[1,0,6,0],[1,1,6,1]],"flags":["formulas_cached_only"]}
["任务名称","企业名称","名录类别","行业类别","受纳水体","执行标准名称","执行标准条目名称","监测点","监测项目","监测日期","流量(m³/s)","水温(°C)","生产负荷(%)","进口浓度","排放浓度","上限","下限","单位","是否超标","超标倍数","备注","是否有评价限值"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","氨氮（NH3-N）","2024-10-31","","22.9","","23.0","0.20","5;8","","mg/L","否","","","是"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","pH值","2024-10-31","","22.9","","7.5","6.9","9","6","无量纲","否","","","是"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","悬浮物","2024-10-31","","22.9","","790","5.5","10","","mg/L","否","","","是"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","化学需氧量","2024-10-31","","22.9","","980","11","50","","mg/L","否","","","是"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","动植物油","2024-10-31","","22.9","","<0.06","<0.06","1","","mg/L","否","","","是"]
["江苏金陵环境股份有限公司城北污水处理厂","江苏金陵环境股份有限公司城北污水处理厂","水环境","污水处理及其再生利用","","城镇污水处理厂污染物排放标准[国标](GB18918-2002)","（表1）基本控制项目最高允许排放浓度（日均值）,一级标准（水温＞12℃或≤12℃）,A标准,通用","排放口DW001(DW001)","石油类","2024-10-31","","22.9","","<0.06","<0.06","1","","mg/L","否","","","是"]