{"text_format":"3","workbook":"xls","n_sheets":4,"sheets":["废水比对","废气排放","废水排放","无组织"],"not_rendered":{"external_links":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废水比对","index":0,"n_rows":11,"n_cols":14,"rows_kept":11,"merged":[[1,0,10,0],[1,1,5,1],[6,1,10,1]],"flags":["formulas_cached_only"]}
["任务名称","企业名称","名录类别","行业类别","执行标准名称","执行标准条目名称","监测点","监测项目","监测日期","样品类型","手动监测值","自动监测值","比对结果","技术要求"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","水环境","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表1）传染病、结核病医疗机构水污染物排放限值在（日均值）,采用其他消毒方式","污水排放口(DW001)","化学需氧量","2024-12-17","实际样","108","97","-10.19%","相对误差不超过±15%"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","水环境","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表1）传染病、结核病医疗机构水污染物排放限值在（日均值）,采用其他消毒方式","污水排放口(DW001)","化学需氧量","2024-12-17","实际样","66","76","15.15%","相对误差不超过±20%"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","水环境","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表1）传染病、结核病医疗机构水污染物排放限值在（日均值）,采用其他消毒方式","污水排放口(DW001)","化学需氧量","2024-12-17","实际样","50","56","12%","相对误差不超过±30%"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","水环境","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表1）传染病、结核病医疗机构水污染物排放限值在（日均值）,采用其他消毒方式","污水排放口(DW001)","化学需氧量","2024-12-17","标准样","250","239","-4.4%","相对误差不超过±10%"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","水环境","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","pH值","2024-12-17","实际样","7.5","7.8","0.3pH","绝对误差不超过±0.5pH"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","水环境","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口DW001","pH值","2024-12-10","实际样","7.3","7.2","-0.1pH","绝对误差不超过±0.5pH"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","水环境","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表1）传染病、结核病医疗机构水污染物排放限值在（日均值）,采用其他消毒方式","污水排放口DW001","化学需氧量","2024-12-10","实际样","124","118","-4.84%","相对误差不超过±15%"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","水环境","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表1）传染病、结核病医疗机构水污染物排放限值在（日均值）,采用其他消毒方式","污水排放口DW001","化学需氧量","2024-12-10","实际样","119","110","-7.56%","相对误差不超过±15%"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","水环境","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表1）传染病、结核病医疗机构水污染物排放限值在（日均值）,采用其他消毒方式","污水排放口DW001","化学需氧量","2024-12-10","实际样","115","108","-6.09%","相对误差不超过±15%"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","水环境","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表1）传染病、结核病医疗机构水污染物排放限值在（日均值）,采用其他消毒方式","污水排放口DW001","化学需氧量","2024-12-10","标准样","250","238","-4.8%","相对误差不超过±10%"]

{"sheet":"废气排放","index":1,"n_rows":21,"n_cols":24,"rows_kept":21,"merged":[[1,0,20,0],[1,1,20,1]],"flags":["formulas_cached_only"]}
["任务名称","企业名称","名录类别","行业类别","执行标准名称","执行标准条目名称","监测点","监测项目","监测日期","流量(m³/h)","温度(°C)","湿度(%)","含氧量(%)","流速(m/s)","生产负荷(%)","实测浓度","折算浓度","上限","下限","单位","是否超标","超标倍数","备注","是否有评价限值"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","焊接废气排放口QF5","颗粒物","2024-12-27","17131","12.7","3.1","","6","","1.3","1.3","20","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","发电机喷漆房废气排放口QF1","苯","2024-12-27","76286","11.5","2","","15.4","","<0.009","<0.009","1","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","发电机喷漆房废气排放口QF1","二甲苯","2024-12-27","76286","11.5","2","","15.4","","<0.009","<0.009","10","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","发电机喷漆房废气排放口QF1","非甲烷总烃","2024-12-27","76286","11.5","2","","15.4","","2.63","2.63","60","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","发电机喷漆房废气排放口QF1","颗粒物","2024-12-27","76286","11.5","2","","15.4","","1.5","1.5","20","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","发电机喷漆房废气排放口QF1","甲苯","2024-12-27","76286","11.5","2","","15.4","","0.034","0.034","10","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","压力容器车间喷漆废气排放口QF2","二甲苯","2024-12-27","20556","11.6","2.1","","5.2","","0.868","0.868","10","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","压力容器车间喷漆废气排放口QF2","非甲烷总烃","2024-12-27","20556","11.6","2.1","","5.2","","6.69","6.69","60","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","压力容器车间喷漆废气排放口QF2","颗粒物","2024-12-27","20556","11.6","2.1","","5.2","","1.7","1.7","20","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","压力容器车间喷漆废气排放口QF2","甲苯","2024-12-27","20556","11.6","2.1","","5.2","","<0.009","<0.009","10","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","压力容器车间喷漆废气排放口QF2","苯","2024-12-27","20556","11.6","2.1","","5.2","","<0.009","<0.009","1","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","危废库废气排放口QF6","苯","2024-12-27","1039","10","2.2","","2.4","","<0.009","<0.009","1","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","危废库废气排放口QF6","二甲苯","2024-12-27","1039","10","2.2","","2.4","","1.27","1.27","10","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","危废库废气排放口QF6","甲苯","2024-12-27","1039","10","2.2","","2.4","","0.047","0.047","10","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","危废库废气排放口QF6","非甲烷总烃","2024-12-27","1039","10","2.2","","2.4","","1.02","1.02","60","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","冲压车间涂漆废气排放口QF3","颗粒物","2024-12-27","3320","16.4","2.3","","13.9","","4.5","4.5","20","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","冲压车间涂漆废气排放口QF3","非甲烷总烃","2024-12-27","3320","16.4","2.3","","13.9","","19.6","19.6","60","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","冲压车间涂漆废气排放口QF3","二甲苯","2024-12-27","3320","16.4","2.3","","13.9","","1.15","1.15","10","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","冲压车间涂漆废气排放口QF3","苯","2024-12-27","3320","16.4","2.3","","13.9","","<0.009","<0.009","1","","mg/m3","否","","","是"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","南京汽轮电机（集团）有限责任公司","水环境,大气环境","汽轮机及辅机制造","大气污染物综合排放标准（江苏省）(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","冲压车间涂漆废气排放口QF3","甲苯","2024-12-27","3320","16.4","2.3","","13.9","","<0.009","<0.009","10","","mg/m3","否","","","是"]

{"sheet":"废水排放","index":2,"n_rows":11,"n_cols":22,"rows_kept":11,"merged":[[1,0,10,0],[1,1,5,1],[6,1,10,1]],"flags":["formulas_cached_only"]}
["任务名称","企业名称","名录类别","行业类别","受纳水体","执行标准名称","执行标准条目名称","监测点","监测项目","监测日期","流量(m³/s)","水温(°C)","生产负荷(%)","进口浓度","排放浓度","上限","下限","单位","是否超标","超标倍数","备注","是否有评价限值"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","水环境","综合医院","","医疗机构水污染物排放标准(GB18466-2005)","（表1）传染病、结核病医疗机构水污染物排放限值在（日均值）,采用其他消毒方式","污水排放口(DW001)","动植物油","2024-12-17","","17.1","","","0.27","20","","mg/L","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","水环境","综合医院","","医疗机构水污染物排放标准(GB18466-2005)","（表1）传染病、结核病医疗机构水污染物排放限值在（日均值）,采用其他消毒方式","污水排放口(DW001)","化学需氧量","2024-12-17","","17.1","","","80","250","","mg/L","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","水环境","综合医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","石油类","2024-12-17","","17.1","","","1.85","20","","mg/L","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","水环境","综合医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","pH值","2024-12-17","","17.1","","","7.6","9","6","无量纲","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","水环境","综合医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口(DW001)","悬浮物","2024-12-17","","17.1","","","51","60","","mg/L","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","水环境","综合医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口DW001","动植物油","2024-12-10","","15.1","","","0.29","20","","mg/L","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","水环境","综合医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口DW001","悬浮物","2024-12-10","","15.1","","","55","60","","mg/L","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","水环境","综合医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口DW001","pH值","2024-12-10","","15.1","","","7.2","9","6","无量纲","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","水环境","综合医院","","医疗机构水污染物排放标准(GB18466-2005)","（表1）传染病、结核病医疗机构水污染物排放限值在（日均值）,采用其他消毒方式","污水排放口DW001","化学需氧量","2024-12-10","","15.1","","","119","250","","mg/L","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","水环境","综合医院","","医疗机构水污染物排放标准(GB18466-2005)","（表2）综合医疗机构和其他医疗机构水污染物排放限值（日均值）,采用其他消毒方式,预处理标准","污水排放口DW001","石油类","2024-12-10","","15.1","","","1.27","20","","mg/L","否","","","是"]

{"sheet":"无组织","index":3,"n_rows":21,"n_cols":20,"rows_kept":21,"merged":[[1,0,20,0],[1,1,20,1]],"flags":["formulas_cached_only"]}
["任务名称","企业名称","名录类别","行业类别","执行标准名称","执行标准条目名称","监测点","监测项目","监测日期","风向","风速（m/s）","温度(℃)","压力（kPa）","排放浓度","上限","下限","单位","是否超标","超标倍数","备注"]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW2","颗粒物","2024-12-27","东北","1.9","5.25","103","0.206","0.5","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW2","苯","2024-12-27","东北","1.9","5.25","103","0.0595","0.1","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW2","二甲苯","2024-12-27","东北","1.9","5.25","103","0.148","0.2","","mg/L","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW2","NMHC","2024-12-27","东北","1.9","5.25","103","2.63","4","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW2","甲苯","2024-12-27","东北","1.9","5.25","103","0.0595","0.2","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW4","二甲苯","2024-12-27","东北","1.9","5.25","103","0.0510","0.2","","mg/L","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW4","颗粒物","2024-12-27","东北","1.9","5.25","103","0.204","0.5","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW4","NMHC","2024-12-27","东北","1.9","5.25","103","2.23","4","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW4","苯","2024-12-27","东北","1.9","5.25","103","0.0655","0.1","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW4","甲苯","2024-12-27","东北","1.9","5.25","103","0.0470","0.2","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW3","苯","2024-12-27","东北","1.9","5.25","103","0.0931","0.1","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW3","甲苯","2024-12-27","东北","1.9","5.25","103","0.0564","0.2","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW3","NMHC","2024-12-27","东北","1.9","5.25","103","2.36","4","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW3","二甲苯","2024-12-27","东北","1.9","5.25","103","0.123","0.2","","mg/L","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界下风向QW3","颗粒物","2024-12-27","东北","1.9","5.25","103","0.209","0.5","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界上风向QW1","NMHC","2024-12-27","东北","1.9","5.25","103","2.70","4","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界上风向QW1","颗粒物","2024-12-27","东北","1.9","5.25","103","0.182","0.5","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界上风向QW1","苯","2024-12-27","东北","1.9","5.25","103","0.0333","0.1","","mg/m3","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界上风向QW1","二甲苯","2024-12-27","东北","1.9","5.25","103","0.0563","0.2","","mg/L","否","",""]
["南京汽轮电机（集团）有限责任公司、招商局金陵船舶（南京）有限公司","招商局金陵船舶（南京）有限公司","水环境,大气环境","铁路、船舶、航空航天和其他运输设备制造业","大气污染物综合排放标准（江苏省地方标准）(DB32/4041-2021)","表3","厂界上风向QW1","甲苯","2024-12-27","东北","1.9","5.25","103","0.0321","0.2","","mg/m3","否","",""]