{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["废气排放","无组织"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废气排放","index":0,"n_rows":40,"n_cols":24,"rows_kept":40,"merged":[[1,0,39,0],[1,1,29,1],[30,1,39,1]],"flags":["formulas_cached_only"]}
["任务名称","企业名称","名录类别","行业类别","执行标准名称","执行标准条目名称","监测点","监测项目","监测日期","流量(m³/h)","温度(°C)","湿度(%)","含氧量(%)","流速(m/s)","生产负荷(%)","实测浓度","折算浓度","上限","下限","单位","是否超标","超标倍数","备注","是否有评价限值"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科废气排放口DA005","氯化氢","2025-05-20","","33.5","2.2","4.8","5.2","","1.75","1.756","10","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科废气排放口DA005","二甲苯（总量）","2025-05-20","","","","","","","0.112","0.112","10","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科废气排放口DA005","甲醛","2025-05-20","","","","","","","0.63","0.63","5","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科废气排放口DA005","甲苯","2025-05-20","","","","","","","<0.0015","<0.0015","10","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科废气排放口DA005","硫酸雾","2025-05-20","","","","","","","<0.20","<0.20","5","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科废气排放口DA005","非甲烷总烃","2025-05-20","","","","","","","1.70","1.70","60","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科DA006","氯化氢","2025-05-20","","29.3","2.3","4.8","6.4","","0.73","0.73","10","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科DA006","甲苯","2025-05-20","","","","","","","<0.0015","<0.0015","10","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科DA006","硫酸雾","2025-05-20","","","","","","","<0.20","<0.20","5","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科DA006","非甲烷总烃","2025-05-20","","","","","","","0.84","0.84","60","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科DA006","二甲苯（总量）","2025-05-20","","","","","","","<0.0015","<0.0015","10","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科DA006","甲醛","2025-05-20","","","","","","","1.32","1.32","5","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","恶臭污染物排放标准(GB14554-93)","（表2）恶臭污染物排放标准值,排气筒高度15m","废气排放口DA003","硫化氢","2025-05-20","","22.4","2.2","","7.7","","0.0039","0.0039","0.33","","kg/h","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","恶臭污染物排放标准(GB14554-93)","（表2）恶臭污染物排放标准值,排气筒高度15m","废气排放口DA003","氨","2025-05-20","","","","","","","0.0094","0.0094","4.9","","kg/h","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","恶臭污染物排放标准(GB14554-93)","（表2）恶臭污染物排放标准值,排气筒高度15m","废气排放口DA003","臭气浓度","2025-05-20","","","","","","","<10","<10","2000","","无量纲","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科DA007","甲醛","2025-05-21","","30.4","2.2","4.9","2.5","","0.62","0.62","5","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科DA007","非甲烷总烃","2025-05-21","","","","","","","2.01","2.01","60","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科DA007","氯化氢","2025-05-21","","","","","","","1.28","1.28","10","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科DA007","硫酸雾","2025-05-21","","","","","","","<0.20","<0.20","5","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科DA007","甲苯","2025-05-21","","","","","","","<0.0015","<0.0015","10","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","病理科DA007","二甲苯（总量）","2025-05-21","","","","","","","0.0324","0.0324","10","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","燃气中央空调废气口DA009","氮氧化物","2025-05-27","","56.2","5.9","4.4","1.5","","145","145","100","","mg/m3","是","0.45","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省地方标准大气污染物综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值,其他","燃气中央空调废气口DA009","二氧化硫","2025-05-27","","","","","","","<3","<3","200","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省大气综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值","废气排放口DA004","氯化氢","2025-05-20","","30.2","2.1","4.2","2.5","","2.3","2.3","10","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","恶臭污染物排放标准(GB14554-93)","（表2）恶臭污染物排放标准值,排气筒高度15m","废气排放口DA004","硫化氢","2025-05-20","","","","","","","0.00369","0.00369","0.33","","kg/h","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","恶臭污染物排放标准(GB14554-93)","（表2）恶臭污染物排放标准值,排气筒高度15m","废气排放口DA004","氨","2025-05-20","","","","","","","0.0039","0.0039","4.9","","kg/h","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省大气综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值","废气排放口DA004","硫酸雾","2025-05-20","","","","","","","<0.20","<0.20","5","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","江苏省大气综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值","废气排放口DA004","非甲烷总烃","2025-05-20","","","","","","","0.58","0.58","60","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","恶臭污染物排放标准(GB14554-93)","（表2）恶臭污染物排放标准值,排气筒高度15m","废气排放口DA004","臭气浓度","2025-05-20","","","","","","","26","26","2000","","无量纲","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","大气环境,环境风险管控","综合医院","江苏省地方标准锅炉大气污染物排放标准(DB32/4385-2022)","表 1 锅炉大气污染物排放浓度限值,燃气锅炉","锅炉废气排放口DA008","二氧化硫","2025-05-29","","","","","","","<3","<3","35","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","大气环境,环境风险管控","综合医院","江苏省地方标准锅炉大气污染物排放标准(DB32/4385-2022)","表 1 锅炉大气污染物排放浓度限值,燃气锅炉","锅炉废气排放口DA008","氮氧化物","2025-05-29","","","","","","","29","38","50","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","大气环境,环境风险管控","综合医院","江苏省大气综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值","危废仓库排气筒DA004","硫酸雾","2025-05-29","","","","","","","<0.20","<0.20","5","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","大气环境,环境风险管控","综合医院","江苏省大气综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值","危废仓库排气筒DA004","氯化氢","2025-05-29","","","","","","","2.45","2.45","10","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","大气环境,环境风险管控","综合医院","江苏省大气综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值","危废仓库排气筒DA004","非甲烷总烃","2025-05-29","","","","","","","0.54","0.54","60","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","大气环境,环境风险管控","综合医院","江苏省大气综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值","病理科废气排放筒DA006","二甲苯","2025-05-29","","","","","","","<0.0015","<0.0015","10","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","大气环境,环境风险管控","综合医院","江苏省大气综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值","病理科废气排放筒DA006","甲醛","2025-05-29","","","","","","","0.25","0.25","20","","mg/m3","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","大气环境,环境风险管控","综合医院","恶臭污染物排放标准(GB14554-93)","（表2）恶臭污染物排放标准值,排气筒高度60m","污水处理站排气筒DA003","硫化氢","2025-05-29","","","","","","","0.0000497","0.0000497","5.2","","kg/h","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","大气环境,环境风险管控","综合医院","恶臭污染物排放标准(GB14554-93)","（表2）恶臭污染物排放标准值,排气筒高度>=60m","污水处理站排气筒DA003","臭气浓度","2025-05-29","","","","","","","112","112","60000","","无量纲","否","","","是"]
["江苏省人民医院、东南大学附属中大医院","东南大学附属中大医院","大气环境,环境风险管控","综合医院","江苏省大气综合排放标准(DB32/4041-2021)","表1 大气污染物有组织排放限值","病理科废气排放筒DA007","二甲苯","2025-05-29","","","","","","","<0.0015","<0.0015","10","","mg/m3","否","","","是"]

{"sheet":"无组织","index":1,"n_rows":6,"n_cols":20,"rows_kept":6,"merged":[[1,0,5,0],[1,1,5,1]],"flags":["formulas_cached_only"]}
["任务名称","企业名称","名录类别","行业类别","执行标准名称","执行标准条目名称","监测点","监测项目","监测日期","风向","风速（m/s）","温度(℃)","压力（kPa）","排放浓度","上限","下限","单位","是否超标","超标倍数","备注"]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表3）污水处理周边大气污染物最高允许浓度","污水处理站周边","氨","2025-05-20","","","","","0.676","1.0","","mg/m3","否","",""]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表3）污水处理周边大气污染物最高允许浓度","污水处理站周边","氯气","2025-05-20","","","","","0.50","0.1","","mg/m3","是","4.00",""]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表3）污水处理周边大气污染物最高允许浓度","污水处理站周边","硫化氢","2025-05-20","","","","","0.007","0.03","","mg/m3","否","",""]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表3）污水处理周边大气污染物最高允许浓度","污水处理站周边","臭气浓度","2025-05-20","","","","","<10","10","","无量纲","否","",""]
["江苏省人民医院、东南大学附属中大医院","江苏省人民医院","大气环境,环境风险管控","综合医院","医疗机构水污染物排放标准(GB18466-2005)","（表3）污水处理周边大气污染物最高允许浓度","污水处理站周边","甲烷","2025-05-20","","","","","<1","1","","%","否","",""]